## Sheet1
Question | OptionA | OptionB | OptionC | OptionD | OptionE | Answer | QuestionLevel
The size of the earth or ground wire is based on the | Maximum fault current carrying through the ground wire. | Rated current carrying capacity of the service wire. | Depends on the soil resisatnce | Both A and C | None of these | D | L
A Safety Electrical One Line Diagram should be used to ______________ all sources of electrical energy. | Identify | Castigate | Evaluate | Modify | All of these | A | M
The dielectric strength of transformer oil is expected to be | 1 kV | 33 kV | 100 kV | 150 kV | 330 kV | B | H
Noise level test in a transformer is a | Special test | Routine test | Type test | All of these | None of these | C | H
Which of the following is not a routine test on transformers ? | Core insulation voltage test | Impedance test | Radio interference test | Polarity test | None of these | C | H
A common method of cooling a power transformer is | Natural air cooling | Oil cooling | Air blast cooling | Any of the above | None of these | B | M
Earth pit value resistance is measures in which type of meter | Insulation megger | Earth megger | volt meter | Am meter | None of these | B | M
Which type fire extinguisher is used for electrical fire | Co2 & dry powder | Foam | Water | All of these | None of these | A | L
Which among these tests are included in high voltage tests? | Power wet test | Impulse voltage withstand tests | Power frequency withstand test 1 minute dry | Only a and b | All of these | D | M
What does IC 01 describe? | Self cooled open machine fan mounted on the shaft | Totally enclosed machine frame cooled no extra fan | Totally enclosed machines frame and tubes externally and internal fault. | Inlet pipe self ventilated machines fan mounted on the shaft. | None of these | A | H
What is the main cause of harmful vibrations in the machine? | Mechanically unbalanced rotor | Bent or cracked shaft | An excessively pulsating load | All of these | None of these | D | M
Which statement is true, with respect to the motor installation? | Wood work is used for mounting switchgears. | All equipments used in power wiring shall be of iron clad. | Looping of conductors is usually made. | The length of flexible conduit is more than 3 m. | All of these | B | H
Which type of enclosure is provided for DC motors used in coal handling plants? | Screen protected | Open type | Totally enclosed fan cooled | Drip proof | Totally enclosed | C | M
Which test is conducted to confirm the withstanding capabilities of insulation? | One minute power frequency withstand test | Lightning impulse withstand test | Switching impulse withstand test | All of these | None of these | D | H
What data is provided from the no load test on induction motors? | Core loss only | Magnetising current | No load power factor | All of these | None of these | C | L
What is meant by Creepage Distance? | Shortest distance between two conducting parts along a stretched string. | Shortest distance between two conducting parts along the surface of the insulating material. | Distance between ground and the highest earthed point on the equipment. | All of these | None of these | B | M
Which among these types of bus bars can be used outdoor? | Tubular | ACSR | AAC | All of these | None of these | D | L
Corona rings are fixed on which among these? | At cross arm end of the string assembly | At corners of bus bar joints | Only at contacts of isolators | Only b and c | All of these | E | M
What is the slip equation using stroboscopic method? | Slip = (apparent rpm / 120 ) * pair of poles | Slip = (apparent rpm / 60 ) * pair of poles | Slip = (apparent rpm / 150 ) * pair of poles | Slip = (apparent rpm / 30 ) * pair of poles | Slip = (apparent rpm / 90 ) * pair of poles | B | H
What should be the permissible sag in meters between two towers if the voltage to be carried is 66 kV? | 2 – 4 m | 5 – 7 m | 4 – 5 m | 1.5 m | 1 m | A | H
What is dielectric absorption ratio? | (InR 30 s) / (InR 60 s) | (InR 60 s) / (InR 30 s) | (InR 10 s) / (InR 60 s) | (InR 60 s) / (InR 10 s) | (InR 30 s) / (InR 10 s) | B | M
Which among these is the cause of sparking at brushes in DC motor? | Defective brushes | Defect in Commutator | Excessive load | Only a and b | All of these | D | M
What is / are the main causes for the noise in the machine? | Magnetostriction | Aerodynamics | Bearing noise of rotating shaft | Only b and c | All of these | D | L
What is the polarization index value for a class A type insulation? | 1.5 | 2 | 2.5 | Less than 1 | Equal to 1 | A | L
What is the maximum temperature limit up to which class E insulation can be used? | 120 °C | 180 °C | 50 °C | 90 °C | 105 °C | A | M
What is the possible cause if the slip ring induction motor fails to start? | Open rheostat | Overload | Brushes do not touch collector rings | Only B and C | All of these | D | L
Which among these is a procedure used for the alignment of shaft? | Axial positioning of the shaft | Paralleling of the shaft axis | Centring of shaft axis | Only A and C | All of these | D | L
Which test is a special type of test performed on the transformers? | Partial discharge | Temperature rise test | Ratio and polarity test | Noise level test | None of these | A | H
Which enclosures are preferred for preventing entry of falling water or dirt? | Totally enclosed | Drip splash or hose proof | Open end bracket | All of these | None of these | B | H
Which among these tests are performed periodically? | Repair tests | Maintenance testing | Manufacturers tests | All of these | None of these | B | M